## Bill of Materials
4242 Campus Point, 5th Flr TI
Bill Of Materials
WSHP Units
Item | Quantity | Description | Part # | Manufacturer
1 | 3 | Application Controller for RHT Units (DAC-322) | 323230 | Delta
3 | 3 | Network Wall Temperature Sensor w/LCD & Setpoint Adjustment (eZNS-T100-B-SM-003-WWG) | 335641 | Delta
4 | 3 | RIB Transformer 40VA, 120-24V (TR40VA001) | 403573 | Delta
5 | 3 | BA/10K-3-D 8" Duct Temp Sensor, 8" Stainless Steel Probe | 401848 | Delta
6 | 3 | Pull Box, NEMA 1, Screw Cover, 12" x 12' x 6", Painted, KOs | SC121206 | Rexel USA
7 | 3 | RHT Valves/Actuators - See provided schedule for more details | See Schedule | Belimo
Alarm Monitoring
Item | Quantity | Description | Part # | Manufacturer
2 | 1 | Application Controller for Alarm Monitoring (DAC-304) | 323053 | Delta
6 | 1 | RIB Transformer 40VA, 120-24V (TR40VA001) | 403573 | Delta
7 | 1 | Pull Box, NEMA 1, Screw Cover, 12" x 12' x 6", Painted, KOs | SC121206 | Rexel USA
Notes
1. Valves provided by Automated Controls, Inc. Valves to be installed by mechanical contractor
2. Automated Controls, Inc. to relocate (10) existing thermostats and (7) existing controllers.

## DAC-322 WSHP
4242 Campus Point, 5th Flr TI
DAC-322 Controller Points List for RHT Unit (Typ. of 3)
Input | Type | Description | Output | Type | Description
IP1 | Reference (1) | Space Temp (ref) | OP1 | Binary (24 VAC) | Spare
IP2 | Analog (10K Type III) | Supply Air Temperature | OP2 | Binary (24 VAC) | Spare
IP3 | Univ. | Spare | OP3 | Analog (10VDC) | RHT Valve Cmnd
IP101 | Linknet | Wall Module Temp (eZNS) | OP4 | Analog (10VDC) | Spare
Notes:
1. Space Temperature (IP1) references the wall module (eZNS) built-in temperature sensor, IP101.

## DAC-304 Alarm Mon
4242 Campus Point, 5th Flr TI
DAC-304 Controller Points List for Alarm Monitoring (Typ. Of 1)
Input | Type | Description | Output | Type | Description
IP1 | Univ. | Spare | OP1 | Binary (24VAC) | Spare
IP2 | Binary (Dry-Contact) | CO2 Manifold Alarm | OP2 | Binary (24VAC) | Spare
IP3 | Univ. | Spare | OP3 | Binary (24VAC) | Spare
|  |  | OP4 | Binary (24VAC) | Spare
Notes:
1. ACME #S700 HP CO2 Manifold to provide dry contact for CO2 alarm point.